## Slide 1
Efficient Calculation of Earth Fault Currents in Compensated Networks
Univ.-Prof. Dipl.-Ing. Dr.techn. Lothar Fickert
Dipl.-Ing. Elisabeth Hufnagl
Dipl.-Ing. Dr.techn. Ernst Schmautzer
Universität Graz
Institute of Electrical Power Systems
www.ifea.tugraz.at
lothar.fickert@tugraz.at

## Slide 2
AGENDA
Efficient Calculation of Fault Currents
Symmetrical components (simplifications)
Global Earthsystem
Definition
Fault current distribution
Assess
(Statik valuation of the safety of persons)
Endangering of persons
Cost Benefit Analysis, CBA

## Slide 3
Theory and Reality of the Earth fault events

## Slide 4
I0 = IE / 3
= (Ipet –Icap) / 3
XPet0 = 3 • UN / IPet
Xcap0 = 3 • UN / Icap
Rc0 = 3 • Rc
Fault calculation in symmetrical components

## Slide 5
Isolated network
Circuit diagram

## Slide 6
Starpoint
IF = Igrid,cap,e/f = lcable·i’ cable + lOHL·i’OHL
Isolated network
Circuit diagram

## Slide 7
Isolated network
IF = UN / √Rc2 + Xgrid,cap2
without factor 3
Equivalent circuit

## Slide 8
IF = UN/ √Rü2+ Xgrid,total2
Exactness, e.g. for Rc = 0:
Z1 = (UN/√3) / Ik
Xgrid,total = (UN/√3) / (v • Icap)
IF = 3 * (UN / √3) / (2 Z1 + 3 • Xgrid,total)
= (UN / √3) / (2/3 • Z1 + Xgrid,total)
≈ (UN/√3) / [Xgrid,total * (1 - 2/3Z1 / Xgrid,total)]
Δ = 2 / 3 • Z1 / Xgrid,total = …
Because Z1 = UN / √3 / IF
respectively. Xgrid,total= UN / √3 / (v • Icap)
… = 2/3 • (v • Icap) / Ik
= 2/3 • 60A / 4000A
Δ = 1%
Whithout factor 3
Compensated network
Equivalent circuit

## Slide 9
Compensated network
IF = p250 • (UN / √3) / √ Rc2 + [Xgrid,cap,,250 - (1 + k0) • XL,250]2
Whithout factor 3
Harmonic-Equivalent circuit

## Slide 10
Compensated network
Electrical diagram

## Slide 11
IF= UPhase / [(RStp // j·Xgrid,total) + ZL (1 + k0) + Rc ]
Compensated network
Equivalent circuit diagram

## Slide 12
Efficient Calculation of Earth Fault Currents in Compensated Networks
Univ.-Prof. Dipl.-Ing. Dr.techn. Lothar Fickert
Dipl.-Ing. Elisabeth Hufnagl
Dipl.-Ing. Dr.techn. Ernst Schmautzer
Universität Graz
Institute of Electrical Power Systems
www.ifea.tugraz.at
lothar.fickert@tugraz.at