## Slide 1: Evaluation of an urban medium voltage network using reliability indices

## Slide 2: Agenda
  Aim of the evaluation
  Reliability assessment
  Restructuring of an urban medium voltage network and results
  Conclusions

## Slide 3: Aim of the evaluation
Assessment of reliability indices of a medium voltage network in order to:
  Evaluate restructuring measures in terms of efficiency
  Impartially compare restructuring measures

## Slide 4: Reliability assessment
  Input data: interruption behavior of network equipment (cables, overhead lines, switches, ...)
  Reliability datatypes: global input for software
  Datatypes, switching options and switching times  reliability values for each network element

## Slide 5: Reliability assessment – reliability datatype

## Slide 6: Reliability assessment – reliability values
Acronym | Reliability value | Unit | Description
F | Expected value of interruption frequency | 1/yr | Frequency of expected interruptions per year
Q | Non-availability | min/yr or h/yr | Probability of expected interruptions per year
T | Expected value of duration of interruption | min or h | Expected duration of interruption

## Slide 7: Reliability assessment – reliability indices
Input data: interruption
behavior in terms of
interruption durations
and frequencies
Reliability-
datatypes
Reliability values
(F, Q and T) for each node
Transformer capacity
respectively number of
customers
Calculation acc. to
IEEE Std.1366-2012
Reliability indices
SAIDI, SAIFI, etc.
Network calculation
software NEPLAN®

## Slide 8: Reliability assessment – reliability indices
  System Average Interruption Duration Index (SAIDI) ...total duration of interruption for the average customer
  System Average Interruption Frequency Index (SAIFI) ...indicates how often the average customer is affected by an interruption
  Customer Average Interruption Duration Index (CAIDI) ...average time required to restore service

## Slide 9: Reliability assessment – reliability indices
  Average System Interruption Duration Index (ASIDI) ...corresponds to SAIDI but refers to the interrupted load rather than to the average customer
  Average System Interruption Frequency Index (ASIFI) ...is based on the load which can't be supplied due to interruptions

## Slide 10: Reliability assessment – reliability indices

## Slide 11: Restructuring of an urban medium voltage network
Assumption of heavy load conditions  selected cables are loaded with more than 50 % of their capacity
  Change of switching status
  Additional cable connection
  Additional cable with cross connections to existing stations

## Slide 12: Measure a – change of switching status
Busbar
Station x
51 % < 30 %
51 % < 30 %
50 % < 30 %
47 %
22 %
32 %
33 %
Circuit breaker closed
Improvement of SAIDI by 28 % initial value: 6,6 min/yr improved value: 4,8 min/yr

## Slide 13: Measure b – additional cable connection
Busbar
Station x
47 % 21 %
24 %
50 % 24 %
51 % 25 %
51 % 26 %
Circuit breaker open
Additional cable connection between busbar and station x
 Initial and additional cable connection are loaded with about 25 % of their capacity

## Slide 14: Combination of measure a and b
Closed circuit breaker + additional cable connection
  Combines the benefits of measures a and b: Lower load and improved SAIDI
  Reduction of SAIDI by 26,7 % initial value: 6,6 min/yr improved value: 4,8 min/yr

## Slide 15: Measure c
Station x
25 %
25 %
Busbar
Additional cable + cross-connections with open circuit breakers
  Reduced loadflow
  Improved SAIDI by 26,5 % initial value: 6,6 min/yr improved value: 4,8 min/yr

## Slide 16: Conclusions
By the use of the network calculation software NEPLAN® and data of the »FNN-Interruption-Statistics« an assessment of reliability indices can be accomplished with high accuracy.
By applying restructuring measures the load of the equipment can be reduced and the network reliability is improved.
Including further switching options can have a positive effect on the network reliability.

## Slide 17: Conclusions
Simplifying statements regarding the impact of network restructuring measures are difficult to make.
The efficiency of such measures depends on the network structure and has to be calculated and evaluated individually.
Evaluation of restructuring measures using reliability indices before the actual implementation of e.g. new cable connections can be beneficial.

## Slide 18: Thank you for your attention

## Slide 19: Appendix