## Slide 1: ON-LINE IDENTIFIABILITY OF A SYNCHRONOUS GENERATOR BY LINEARIZED EQUIVALENT
Gorazd Bone, Urban Rudež and Rafael Mihalič

## Slide 2: About dynamical equivalents in general
Let there be a dynamic signal measurement.

## Slide 3: About dynamical equivalents in general
Let there be a dynamic signal measurement.
Chart: Dynamical resposne - equivalent

## Slide 4: About dynamical equivalents in general
Try to find a dynamical equivalent
Chart: Dynamical resposne - equivalent

## Slide 5: About dynamical equivalents in general
Try to find a dynamical equivalent
Chart: Dynamical resposne - equivalent

## Slide 6: About dynamical equivalents in general
Quality – how to measure?

## Slide 7: About dynamical equivalents in general
Quality – how to measure?
Chart: Dynamical resposne - equivalent

## Slide 8: About dynamical equivalents in general
Quality – distance between signals
Chart: Dynamical resposne - equivalent

## Slide 9: About dynamical equivalents in general
Quality – distance between signals

## Slide 10: About dynamical equivalents in general
Quality – distance between signals
Usually the sum of suqares of measurement difference is used

## Slide 11: About dynamical equivalents in general
Quality – distance between signals
Usually the sum of suqares of measurement difference is used
The smaller the value of H the better is the equivalent

## Slide 12: Synchronous generator dynamical equivalent

## Slide 13: Synchronous generator dynamical equivalent
Measured signal at terminals – obtained active and reactive power dynamics

## Slide 14: Synchronous generator dynamical equivalent
Measured signal at terminals – obtained active and reactive power dynamics
Use exhaustive, brute force search

## Slide 15: Synchronous generator dynamical equivalent
Measured signal at terminals – obtained active and reactive power dynamics
Use exhaustive, brute force search
  Perform simulation, compare the signals, if close, save parameters

## Slide 16: Synchronous generator dynamical equivalent
Measured signal at terminals – obtained active and reactive power dynamics
Use exhaustive, brute force search
  Perform simulation, compare the signals, if close, save parameters
  Decoupled. Some signals not influenced by some parameters

## Slide 17: Synchronous generator dynamical equivalent
Measured signal at terminals – obtained active and reactive power dynamics
Use exhaustive, brute force search
  Perform simulation, compare the signals, if close, save parameters
  Decoupled. Some signals not influenced by some parameters
The results show that different parameter sets may produce the same dynamics

## Slide 18: Identifiablity issue – active power for all parameters

## Slide 19: Identifiablity issue – reactive power for all parameters

## Slide 20: Noticeable difference between physical and simulated (modeling fidelity)

## Slide 21: Intrinsic issue with synchronous generator
*https://www.tonex.com/fundamentals-of-synchronous-machines/

## Slide 22: Intrinsic issue with synchronous generator
*https://www.tonex.com/fundamentals-of-synchronous-machines/
**Prabhashankar Kundur: „Power System Stability and Control“, McGrawHill Inc.

## Slide 23: Thank you for your attention
Gorazd Bone, Urban Rudež and Rafael Mihalič